## Form 410-2 (IP Units)
CALCULATION OF AIR-SIDE RESISTANCES FROM STEAM AND WATER COIL TESTS (Imperial Units, IP) AHRI CERTIFICATION PROGRAM FOR FORCED-CIRCULATION AIR-COOLING AND AIR-HEATING COILS
Company: | [8 empty] | Date:
Solution Procedure Steps for Specific Coil Application |  |  | Coil Line: |  |  |  |  | Coil Type: | Choose
Coil Surface:
|  |  | GENERAL PROCEDURE | [8 empty] | Choose Surface Condition
Steam Coils | Water Coils |  | General Category | Item No. | Item Abbr. | Item Description |  |  |  | Calculation Procedure | Dimensions | Numerical Input and Formulas
| Dry Surface | Fully-Wetted Surface
1 | 1 | 1 | Coil Physical Data | 1 | Ao | Total External Coil Surface (See Form 410-1) |  |  |  |  | ft2
2 | 2 | 2 |  | 2 | Di | Tube Inside Diameter (See Form 410-1) |  |  |  |  | in
3 | 3 | 3 |  | 3 | B | Surface Ratio (See Form 410-1) |  |  |  |  | --
- | 4 | 4 |  | 4 | Nc | Number of Tube Circuits in Coil |  |  |  |  | --
- | 5 | 5 |  | 5 | Aix | Total Cross-Sectional Fluid Flow Area |  |  |  | = (π/4)*(Di/12)2*Nc | ft2
4 | 6 | 6 |  | 6 | Nr | Coil Depth in Rows |  |  |  |  | --
| 7 | 7 |  | 7 | Ls | Straight Tube Length per Pass |  |  |  |  | in
| 8 | 8 |  | 8 | Ls/Di | Straight Tube Length per Pass/Tube Diameter |  |  |  |  | -
[12 empty] | Test Run 1 | Test Run 2 | Test Run 3 | Test Run 4
5 | 9 | 9 | Laboratory Test Observation and Calculations Obtained from ASHRAE Std 33-2000, Forms 33TD-3 (water) or 33TD-4 (steam) | 9 | Ps | Avg. Absolute Static Pressure at Test Coil |  |  |  |  | in Hg abs
6 | 10 | 10 |  | 10 | t1db | Entering Air Dry-Bulb Temperature |  |  |  |  | °F
- | 11 | 11 |  | 11 | t1wb | Entering Air Wet-bulb Temperature |  |  |  |  | °F
- | - | 12 |  | 12 | h1 | Entering Air Enthalpy |  |  |  |  | Btu/lb
7 | 12 | 13 |  | 13 | t2db | Leaving Air Dry-Bulb Temperature |  |  |  |  | °F
- | - | 14 |  | 14 | h2 | Leaving Air Enthalpy |  |  |  |  | Btu/lb
- | 13 | 15 |  | 15 | tw1 | Entering Water Temperature |  |  |  |  | °F
- | 14 | 16 |  | 16 | tw2 | Leaving Water Temperature |  |  |  |  | °F
- | 15 | 17 |  | 17 | ww | Water Flow Rate |  |  |  |  | lb / h
8 | - | - |  | 18 | tvmg | Mean Saturated Steam Temp in Coil Circuit |  |  |  |  | °F
9 | 16 | 18 |  | 19 | qs | Average Sensible Heat Transfer Capacity |  |  |  |  | Btu/h
- | 17 | 19 |  | 20 | qt | Average Total Heat Transfer Capacity |  |  |  |  | Btu/h
10 | 18 | 20 |  | 21 | va | Standard Air Face Velocity |  |  |  |  | std. ft/min
- | 19 | 21 |  | 22 | twm | Mean Water Temperature Inside Tubes |  |  |  | twm = 0.5(tw1+tw2) | °F | 0 | 0 | 0 | 0
11 | 20 | - |  | 23 | ΔPst | Isothermal Dry Surface Air-Side Pressure Drop at Standard Conditions |  |  |  |  | in H2O
- | - | 22 |  | 24 | ΔPsW | Wet Surface Air-Side Pressure Drop at Standard Conditions |  |  |  |  | in H2O
- | 21 | 23 | CALCULATIONS TO DETERMINE HEAT TRANSFER COEFFICIENTS FOR USE IN APPLICATION RATINGS | 25 | qs/qt | Sensible Heat Ratio - If < 0.95, coil surface is all wet or partially dry. - If ≥ 0.95, coil surface is fully dry. |  |  |  | Ratio = qs/qt | -- | 0 | 0 | 0 | 0
- | 22 | 24 |  | 26 | Vw | Average Standard Water Velocity |  |  |  | = (ww)/(62.361*3600*Aix) | ft/s | 0 | 0 | 0 | 0
12 | 23 | - |  | 27 | Δtm | Logarithmic Mean Temp Difference between Air and Heating or Cooling Fluid
[7 empty] | Select Coil Type Above |  |  |  | °F | 0 | 0 | 0 | 0
[7 empty] | Select Coil Type Above |  |  |  |  | 0 | 0 | 0 | 0
[7 empty] | For Single Tube Steam Coils: |  |  | Δtm = (t2db-t1db) / (ln((tvmg-t1db)/(tvmg-t2db))) | °F | 0 | 0 | 0 | 0
[7 empty] | For Thermal Counterflow* Cold Water Coils: |  |  | Δtm = ((t1db-tw2)-(t2db-tw1))/ (ln((t1db-tw2)/(t2db-tw1))) | °F | 0 | 0 | 0 | 0
[7 empty] | For Thermal Counterflow Hot Water Coils: |  |  | Δtm = ((tw2-t1db)-(tw1-t2db))/ (ln((tw2-t1db)/(tw1-t2db))) | °F | 0 | 0 | 0 | 0
12* | 23* |  |  |  |  | *If other than thermal counter-flow, determine mean temp difference from Appendix D and enter Δtm values in this row for Test Runs 1 thru 4 |  |  |  |  | °F | 0 | 0 | 0 | 0
13 | 24 |  |  | 28 | R | Overall Thermal Resistance Between Air and Heating or Cooling Fluid |  |  |  | R = (Ao*Δtm)/qs | h·ft2·°F /Btu | 0 | 0 | 0 | 0
14 | 25 |  |  | 29 |  | Plot R vs. Va on logarithmic coordinates as shown in Fig. 15. This curve is used in obtaining steam coil application ratings. |  |  |  |  | --
| 26 | 25 |  | 30 | ρw | Density of Water at Mean Water Temp., twm |  |  |  |  | lb/ft3
| 27 | 26 |  | 31 | cpw | Specific Heat of Water at Mean Water Temp., twm |  |  |  |  | Btu/lb·°F
| 28 | 27 |  | 32 | μw | Dynamic Viscosity of Water at Mean Water Temp., twm |  |  |  |  | lb/ft·h
| 29 | 28 |  | 33 | kw | Thermal Conductivity of Water at Mean Water Temp., twm |  |  |  |  | Btu·ft/ h·ft2·°F
| 30 | 29 |  | 34 | Prw | Prandtl Number of Water at Mean Water Temp, twm |  |  |  | = cpw*μw/kw | - | 0 | 0 | 0 | 0
| 31 | 30 |  | 35 | Prw2/3 |  |  |  |  | = (cpw*μw/kw)2/3 | - | 0 | 0 | 0 | 0
| 32 | 31 |  | 36 | Gw | Mass Velocity of Water at Mean Water Temp., twm |  |  |  | = ww/Aix | lb/h·ft2 | 0 | 0 | 0 | 0
| 33 | 32 |  | 37 | Rew | Reynolds Number of Water at Mean Water Temp., twm |  |  |  | Rew = Gw*Di/(12*μw) | -
| 34 | 33 |  | 38 | jw | Colburn j Factor from Fig. 17 with Rew and Ls/Di |  |  |  |  | -
| 35 | 34 |  | 39 | (μtw/ μw).14 init | Initial Estimate Dynamic Viscosity Ratio (VRinit) For water cooling coils use initial estimate of 0.98 and for water heating coils use initial estimate of 1.03
| 36 | 35 |  | 40 | fw(init) | Initial Est. of Water Side Film Heat Transfer Coefficient |  |  |  | jw*cpw*Gw/(Prw2/3*μtw/μw0.14) |  | 0 | 0 | 0 | 0
| 37 | 36 |  | 41 | Rw(init) | Initial Estimate of Tube Side Film Thermal Resistance |  |  |  | B/fw(init) | h·ft2·°F /Btu | 0 | 0 | 0 | 0
| 38 |  |  | 42 | ttwm | Initial Estimate of Mean Tube Wall Temperature |  |  |  | ttwm = twm + (Rw(init)/R)*Δtm | °F | 0 | 0 | 0 | 0
| 39 |  |  | 43 | μtwm | Dynamic Viscosity of Water at Tube Wall Temp., ttwm |  |  |  |  | lb/ft·h | 2.8915 | 2.9984
| 40 |  |  | 44 | (μtw/ μw).14 calc | Calculated Dynamic Viscosity Ratio (VRcalc) If VRinit is not within 2 % of VRcalc , use VRcalc as new VRinit and recalculate starting with Item 39. Otherwise, procede to next step | [5 empty] | 0 | 0 | 0 | 0
| 41 |  |  | 45 | fw | Water-Side Film Heat Transfer Coefficient If VRinit is +/- 2 % of VRcalc , set fw equal to fw(init) * VRcalc / VRinit |  |  |  | fw = fw(init)*VRcalc/VRinit | Btu/ h·ft2·°F | 0 | 0 | 0 | 0
* | 42 |  |  | 46 | Rv | Tube-Side Film Thermal Resistance, Steam |  |  |  | Rv = B/2000 | h·ft2·°F /Btu
[5 empty] | Rw | Tube-Side Film Thermal Resistance, for hot or cold water. |  |  |  | Rw = B(1/fw) | h·ft2·°F /Btu | 0 | 0 | 0 | 0
* | 43 |  |  | 47 | RaD + RmD | Combined Air Film Plus Metal Thermal Resistance. |  |  |  | Equals R - Rv or R - Rw | h·ft2·°F /Btu | 0 | 0 | 0 | 0
Also, plot this vs. Va on logarithmic coord as shown in Fig. 15. This curve is used for all sensible heat coils except steam coils.
* | 44 | 37 |  | 48 | RaD | Air Film Thermal Resistance for Dry Surface. For fully wet coils, use RaD from Fig. 15 as determined from dry coil tests |  |  |  | From Fig. 16, knowing RaD + RmD | h·ft2·°F /Btu
* | 45 |  |  | 49 |  | Plot RaD vs. Va on logarithmic coordinates as shown in Fig. 15. This curve is used in obtaining application ratings for all sensible heat coils except steam coils. |  |  |  |  | --
| 46 | 38 |  | 50 | faD | Air-Side Heat Transfer Coefficient for Dry Surface |  |  |  | faD = 1/RaD | Btu/ h·ft2·°F | 0 | 0 | 0 | 0
| 47 | 39 |  | 51 | RmD | Total Metal Thermal Resistance of Fin and Tube. |  |  |  | Assuming dry surface, obtain from Fig. 14 with faD | h·ft2·°F /Btu
|  | 40 |  | 52 | hm | Mean Air Enthalpy |  |  |  | hm = 0.5(h1+h2) | Btu/lb | 0 | 0 | 0 | 0
|  | 41 |  | 53 | C | Approximate Coil Characteristics (cp assumed to be 0.243. See ASHRAE 33-2016 for further explanation) |  |  |  | = (Rm+Rw)/(0.243*Raw) | lb·°F /Btu | 0 | 0 | 0 | 0
|  | 42 |  | 54 | tsm | Approximate Mean Coil Surface Temp. |  |  |  |  | °F | 57
|  | 43 |  | 55 | m"/cp | Approx. Air-Side Heat Transfer Multiple for Wet Surface Coils. From Equation 6 | [5 empty] | 2.67
|  | 44 |  | 56 | RaW | Air Film Thermal Resistance for Wet Surface Note: Assume this value for trial and error solution. Suggest initial value should be same as RaD. |  |  |  |  | h·ft2·°F /Btu | 0.084
|  | 45 |  | 57 | faW | Approx. Air-Side Heat Transfer Coefficient for Wet Surface |  |  |  | faW = (m"/cp)/RaW | Btu/ h·ft2·°F | 31.7857
|  | 46 |  | 58 | RmW | Total Metal Thermal Resistance of Fin and Tube for Wet Surface From Fig. 14 with faW |  |  |  |  | h·ft2·°F /Btu | 0.013
|  | 47 |  | 59 | C | Coil Characteristic |  |  |  | C = (Rw+RmW)/(0.243*RaW) | lb·°F /Btu | 0.63688 | 0 | 0 | 0
|  | 48 |  | 60 | ttwm | Initial Estimate of Mean Tube Wall Temperature |  |  |  | twm+(Rw/(Rw+RmW))*(tsm-twm) | °F | 0 | 0 | 0 | 0
|  | 49 |  | 61 | μtwm | Dynamic Viscosity of Water at Tube Wall Temp., ttwm |  |  |  |  | lb/ft·h | 2.9534
|  | 50 |  | 62 | (μtw/ μw).14 calc | Calculated Dynamic Viscosity Ratio (VRcalc) If VRinit is not within 2 % of VRcalc , use VRcalc as new VRinit and recalculate starting at Item 39. Otherwise, procede to Item 63 |  |  |  |  | - | 0 | 0 | 0 | 0
|  | 51 |  | 63 | fw | Water-Side Film Heat Transfer Coefficient If VRinit is +/- 2 % of VRcalc , set fw equal to fw(init) * VRcalc / VRinit |  |  |  | fw = fw(init)*VRcalc/VRinit | Btu/ h·ft2·°F | 0 | 0 | 0 | 0
|  | 52 |  | 64 | Rw | Tube-Side Film Thermal Resistance, for hot or cold water. |  |  |  | Rw = B(1/fw) | h·ft2·°F /Btu | 0 | 0 | 0 | 0
|  | 53 |  | 65 | t1dp | Entering Air Dew Point Temperature |  |  |  | From Psychrometric Chart with Ps, t1db, and t1wb | °F
Note: Calculation of Dew Point Temp for Non-Standard Air Pressure*
pv = p'-[((ps-p')*(t1db-t1wb))/(2830-(1.44*t1wb))]
Where: ps = Air Pressure. p' = Sat. Vapor Press. at t1wb from steam tables. Pv = Saturation Vapor Press. at Dew Point Temp.
Note: t1dp = Dew Point Temp. is Saturation Temp. Corresponding to Saturation Vapor Pressure, pv, from Steam Tables.
|  | 54 |  | 66 | ts1 | Coil Surface Temp. on Entering Air Side |  |  |  |  | °F
Determine ts1 by trial and error using equation: ts1 = tw2 + C(h1-hs1). Correct hs1 for Ps, and use h1, tw2 and C. For fully-wetted coil, t1dp ≥ ts1. If t1dp < ts1, coil is partially wet and calculation procedures may be determined from Form 410-6.
|  | 55 |  | 67 | hs1 | Saturated Air Enthalpy at Ps and ts1 |  |  |  |  | Btu/lb
|  | 56 |  | 68 | ts2 | Coil Surface Temp. on Leaving Air Side |  |  |  |  | °F
Eetermine ts2 by trial and error using equation: ts2 = tw1 + C(h2-hs2). Correct hs2 for Ps, and use h2, tw1 and C. If t1dp < ts2, then coil is all dry
|  | 57 |  | 69 | hs2 | Saturated Air Enthalpy at Ps and ts2 |  |  |  |  | Btu/lb
|  | 58 |  | 70 | Δhm | Logarithmic Mean Enthalpy Difference between Air Stream and Coil Surface |  |  |  | Δhm=((h1-hs1)-(h2-hs2)) / (ln((h1-hs1)/(h2-hs2))) | Btu/lb | 0 | 0 | 0 | 0
|  | 59 |  | 71 | Ac | Calculated External Surface Area |  |  |  | Ac =(0.243*RaW*qt)/Δhm | ft2 | 0 | 0 | 0 | 0
|  | 60 |  | 72 |  | Assume other values for RaW (Item 56) and repeat procedure through Ac (Item 71). Plot values of Ac vs. RaW as shown in Fig. F410-2.1. Two or more points shall be plotted so that Ao lies between calculated values of Ac. |  |  |  |  | --
|  | 61 |  | 73 | RaW | Air Film Thermal Resistance for Wet Surface The point on the curve (Fig. F410-2.1) as plotted in the previous step, where Ac = Ao determines the RaW value which corresponds to Va.
|  | 62 |  | 74 |  | Plot RaW vs. Va on logarithmic coordinates as shown in Fig 18.
If the RaW curve is within 15% of the RaD curve, then RaD may be used to obtain application ratings for the wetted surface portion of all cooling and dehumidifying coils.
15 | 48 | 63 | CALCULATION OF COIL AIR-SIDE FRICTION | 75 |  | Coil Air-Side Friction per Row Deep at Standard Conditions
[8 empty] | For dry surface: |  | Will equal ΔPst/Nr | In H20 /Row
[8 empty] | For fully wetted surface: |  | Will equal ΔPsW/Nr | In H20 /Row
16 | 49 | 64 |  | 76 |  | Plot previous step vs. Standard Air Face Velocity, Va, on logarithmic coordinates in appropriate plot based on coil type. Plot both dry and wet surface friction in Fig. 28 These curves are used for application ratings. |  |  |  |  | --
* These items apply when steam coil tests are used to determine RaD for hot water coils
Figure F410-2.1

## Sheet3
113.0973
0.0001131
0.0625
0.19635
0.0013635