## Form 410-4 IP Units
CALCULATION OF REFRIGERANT-SIDE THERMAL RESISTANCES FROM VOLATILE REFRIGERANT COIL TESTS (Imperial Units, IP) AHRI CERTIFICATION PROGRAM FOR FORCED-CIRCULATION AIR-COOLING AND AIR-HEATING COILS
Company | [7 empty] | Date
Solution Procedure Steps for Specific Coil Application |  | Coil Line: |  |  |  |  | Coil Type:
|  | Coil Surface: | [8 empty] | Choose Surface Condition
GENERAL PROCEDURE
Dry Surface | Fully- Wetted Surface | General Category | Item No. | Item Abbr. | Item Description |  |  |  | Calculation Procedure | Dimensions, IP | Numerical Input and Equations
1 | 1 | COIL PHYSICAL DATA | 1 | Ao | Total External Coil Surface (See Form 410-1) |  |  |  |  | ft2
2 | 2 |  | 2 | Di | Tube Inside Diameter (See Form 410-1) |  |  |  |  | in
3 | 3 |  | 3 | Nt | Total Number of Tubes in Coil |  |  |  |  | --
4 | 4 |  | 4 | Lt | Coil Finned Tube Length Exposed to Air Flow |  |  |  |  | in
5 | 5 |  | 5 | B | Surface Ratio (See Form 410-1) |  |  |  |  | --
6 | 6 |  | 6 | Nc | Number of Tube Circuits in Coil |  |  |  |  | --
7 | 7 |  | 7 | Aix | Total Cross-Sectional Fluid Flow Area |  |  |  | (π/4)*(Di/12)2*Nc | ft2 | 0
8 | 8 |  | 8 | Ls | Straight Tube Length per Pass |  |  |  |  | in
9 | 9 |  | 9 | Kb | Equivalent Length of Coil Circuit per Return Bend |  |  |  |  | in
10 | 10 |  | 10 | Le | Total Equivalent Length of Coil Circuit |  |  |  | 1/12*[Ls*(Nt/Nc)+ Kb*(Nt/Nc-1)] | ft | 0
[11 empty] | Test 1 | Test 2 | Test 3 | Test 4
11 | 11 | LABORATORY TEST OBSERVATIONS AND CALCULATIONS OBTAINED FROM AHSRAE STD 33-2000, FORMS 33TD-2 | 11 | Ps | Avg. Absolute Static Pressure at Test Coil |  |  |  |  | in Hg abs
12 | 12 |  | 12 | t1db | Entering Air Dry-Bulb Temperature |  |  |  |  | °F
13 | 13 |  | 13 | t1wb | Entering Air Wet-bulb Temperature |  |  |  |  | °F
| 14 |  | 14 | h1 | Entering Air Enthalpy |  |  |  |  | Btu/lb
14 | 15 |  | 15 | t2db | Leaving Air Dry-Bulb Temperature |  |  |  |  | °F
| 16 |  | 16 | h2 | Leaving Air Enthalpy |  |  |  |  | Btu/lb
15 | 17 |  | 17 | Va | Standard Air Face Velocity |  |  |  |  | ft/min
16 | 18 |  | 18 | Prc2 | Abs. Refrigerant Pressure Leaving Coil Circuits |  |  |  |  | psia
17 | 19 |  | 19 | ΔPrc | Refrigerant Pressure Drop Through Coil Circuit |  |  |  |  | psi
18 | 20 |  | 20 | tr1 | Saturated Liquid Refrigerant Temp Entering Coil Circuits |  |  |  |  | °F
19 | 21 |  | 21 | trc2g | Saturated Refrigerant Temp Leaving Coil Circuits |  |  |  |  | °F
20 | 22 |  | 22 | trc2 | Temperature of Superheated Refrigerant Lvg Coil Circuits |  |  |  |  | °F
21 | 23 |  | 23 | wr | Refrigerant Flow Rate |  |  |  |  | lb/h
22 | 24 |  | 24 | qs | Average Sensible Cooling Capacity |  |  |  |  | Btu/h
23 | 25 |  | 25 | qt | Avg. Total Cooling and Dehumidifying Capacity |  |  |  |  | Btu/h
24 | 26 | CALCULATIONS OF REFRIGERANT-SIDE THERMAL RESISTANCES | 26 | qs/qt | Sensible Heat Ratio - If < 0.95, coil surface is all wet or partially dry. - If ≥ 0.95, coil surface is fully dry. |  |  |  | Ratio = qs/qt | -- | 0 | 0 | 0 | 0
25 | 27 |  | 27 | vrc2g | Specific Volume of Saturated Refrigerant Leaving Coil Circuit (From refrigerant tables with Prc2) |  |  |  |  | ft3/lb
26 |  |  | 28 | RaD + RmD | Combined Air Film Plus Metal Thermal Resistance (From Fig. 4 with Va) |  |  |  |  | h·ft2·°F/Btu
27 |  |  | 29 | Δtm | Overall Logarithmic Mean Temperature Difference between Air and Refrigerant where tr1 > trc2g |  | Choose |  |  |  | 0 | 0 | 0 | 0
[6 empty] | For Thermal Counterflow Coils |  |  | Δtm = ((t1-trl)-(t2-trc2g)) /(ln((t1-trl)/(t2-trc2g))) | °F | 0 | 0 | 0 | 0
[6 empty] | For Thermal Parallel Flow Coils |  |  | Δtm = ((t1-trc2g)-(t2-tr1)) /(ln((t1-trc2g)/(t2-tr1))) | °F | 0 | 0 | 0 | 0
28 |  |  | 30 | R | Overall Thermal Resistance |  |  |  | R = Ao*Δtm/qt | h·ft2·°F/Btu | 0 | 0 | 0 | 0
29 |  |  | 31 | Rr | Film Thermal Resistance of Refrigerant |  |  |  | Rr = R - (RaD + RmD) | h·ft2·°F/Btu | 0 | 0 | 0 | 0
30 |  |  | 32 | fr | Refrigerant-Side Film Heat Transfer Coefficient |  |  |  | fr = B/Rr | h·ft2·°F/Btu | 0 | 0 | 0 | 0
31 |  |  | 33 | qt/Nc | Refrigerant Loading Rate per Tube Circuit |  |  |  | qt/Nc | Btu/h | 0 | 0 | 0 | 0
32 | 28 |  | 34 |  | Pressure Drop Parameter for Volatile Refrigerant |  |  |  | Eq. = ΔPrc/Levrc2g | lb2/ in2·ft4 | 0 | 0 | 0 | 0
33 | 29 |  | 35 | wr/Nc | Volatile Refrigerant Flow Rate per Tube Circuit |  |  |  | Eq. = wr/Nc | lb/h | 0 | 0 | 0 | 0
34 |  |  | 36 |  | Plot Rr/B vs qt/Nc on logarithmic coordinates as shown in Fig. 18. |  |  |  | Rr/B = 1/fr | -- | 0 | 0 | 0 | 0
35 | 30 |  | 37 |  | Plot ΔPrc/LeVrc2g vs wr/Nc on logarithmic coordinates as shown in Fig. 18. This curve is used for application ratings of volatile refrigerant coils. |  |  |  |  | --
| 31 |  | 38 | RaW | Air Film Thermal Resistance for Wet Surface (From Fig. 18 with Va) |  |  |  |  | h·ft2·°F/Btu
| 32 |  | 39 | fr | (Assumed) Refrigerant-Side Film Heat Transfer Coefficient Note: Assume this value for trial and error solution. Suggest initial trial value of 300. |  |  |  |  | Btu/h·ft2·°F
| 33 |  | 40 | Rr | Film Thermal Resistance of Refrigerant |  |  |  | Rr = B/fr | h·ft2·°F/Btu | 0 | 0 | 0 | 0
| 34 |  | 41 | RmW | Approx. Total Metal Thermal Resistance (Wetted Surface) From Fig. 14 with faW = 1/RaW) |  |  |  |  | h·ft2·°F/Btu
| 35 |  | 42 | C | Approximate Coil Characteristic *The approx value of C is used only to obtain the final value of RmW |  |  |  | C = (Rr+RmW)/(0.243*RaW) | lb·°F /Btu | 0 | 0 | 0 | 0
| 36 |  | 43 | hm | Mean Air Enthalpy |  |  |  | hm = 0.5(h1+h2) | Btu/lb | 0 | 0 | 0 | 0
| 37 |  | 44 | trm | Mean Refrigerant Temperature |  |  |  | trm = 0.5(trl+trc2g) | °F | 0 | 0 | 0 | 0
| 38 |  | 45 | tsm | Approx. Mean Surface Temperature. |  |  |  |  | °F
| 39 |  | 46 | m"/cp | Approx. Air-Side Heat Transfer Multiplier for Wet Surface Coils from Equation 6 |  |  |  |  | --
| 40 |  | 47 | faW | Air-Side Heat Transfer Coefficient |  |  |  | faW = (m"/cp)/RaW | Btu/h·ft2·°F | 0 | 0 | 0 | 0
| 41 |  | 48 | RmW | Total Metal Thermal Resistance of Fin and Tube for Wet Surface (From Fig. 14 with faW) |  |  |  |  | h·ft2·°F/Btu
| 42 |  | 49 | C | Coil Characteristic for Wetted Surface |  |  |  | C = (Rr+RmW)/(0.243*RaW) | lb·°F /Btu | 0 | 0 | 0 | 0
| 43 |  | 50 | t1dp | Entering Air Dew Point Temperature Note: Calculation of Dew Point Temp for Non-Standard Air Pressure |  |  |  | From Psychrometric Chart with Ps, t1db, and t1wb | °F
pv, IP = p'-[((ps-p')*(t1-t1wb))/(2830-(1.44*t1wb))]
Where: ps = Air Pressure. p' = Saturation Vapor Press. at t1wb from steam tables. Pv = Saturation Vapor Press. at Dew Point Temp. Note: t1dp (Dew Point Temp) is Saturation Temp Corresponding to Saturation Vapor Pressure pv from Steam Tables
| 44 |  | 51 | ts1 | Coil Surface Temp. on Entering Air Side |  |  |  |  | °F
Determine ts1 by trial and error using equation: ts1 = trl + C(h1-hs1). Correct hs1 for Ps, and use h1, tr1 and C. (For Thermal Parallel flow us trc2g in lieu of tr1 ) For fully-wetted coil, t1dp ≥ ts1. If t1dp < ts1, coil is partially wet and calculation procedures may be determined from Form 410-6.
| 45 |  | 52 | hs1 | Saturated Air Enthalpy at ts1 (From Air Enthalpy Tables with Ps and ts1) |  |  |  |  | Btu/lb
| 46 |  | 53 | ts2 | Coil Surface Temp. on Leaving Air Side |  |  |  |  | °F
Determine ts2 by trial and error using equation: ts2 = trc2g + C(h2-hs2). Correct hs2 for Ps, and use h2, tw1 and C. (For Thermal Parallel Flow use tr1 in lieu of trc2g)
| 47 |  | 54 | hs2 | Saturated Air Enthalpy at ts2 (From Air Enthalpy Tables with Ps and ts1) |  |  |  |  | Btu/lb
| 48 |  | 55 | Δhm | Logarithmic Mean Enthalpy Difference |  |  |  | Δhm=((h1-hs1)-(h2-hs2)) /(ln((h1-hs1)/(h2-hs2))) | Btu/lb | 0 | 0 | 0 | 0
| 49 |  | 56 | Ac | Calculated External Surface Area of Coil |  |  |  | Ac =(0.243*RaW*qr)/Δhm | ft2 | 0 | 0 | 0 | 0
| 50 | PLOTS | 57 |  | Assume other values for fr and repeat procedure through Ac. Plot values of fr vs Ac as shown in Fig. F410-4.1. Two or more points shall be plotted so that Ao lies between calculated values of Ac.
| 51 |  | 58 | fr | Refrigerant Side Film Heat Transfer Coefficient |  |  |  |  | Btu/h·ft2·°F
The point on the curve (Fig. F410-4.1) as plotted in the previous step, where Ac = Ao determines the value of fr corresponding to the circuit loading qt/Nc.
36 | 52 |  | 59 | Rr/B | Film Thermal Resistance of Refrigerant |  |  |  | Rr/B = 1/fr | h·ft2·°F/Btu | 0 | 0 | 0 | 0
| 53 |  | 60 |  | Plot Rr/B vs qt/Nc on logarithmic coordinates as shown in Fig. 18. This curve is used to obtain application ratings. |  |  |  |  | --
Figure F410-4.1