## Pd Adjust
Water Pressure Drop Adjustment Calculations - ref: 550/590 appendix G
Evaporator Piping | [6 empty] | Press Drop Correction (ft) | Press Drop Correction (kPa) | dyn visc (lbm/ft/hr) | L/D | Dia Ratio | calc angle (deg) | Relative Roughness | Reynolds Nbr | Fric factor | K Factor | Area (ft2) | Velocity (ft/sec) |  |  | Typical Steel Pipe Diameters (in)
Upstream Pipe, Water Temperature (F) | 54 | Flow Rate (gpm) | 5000 | [5 empty] | 2.9808 | [11 empty] | Nominal Size/ Sched | ID
Flow Tube Inside Diameter at Static Pressure Measurement Location (inches) | 13.25 | Length (of straight pipe) | 14 | (inches) |  |  | 0.031202 | 0.093148 |  |  |  |  | 0.00013585 | 968145.2313 | 0.014038 |  | 0.95754 | 11.6348 | Material Roughness (ft) | 0.00015 | 1/4, 40 ST | 0.364
Contraction or Enlargement Section (if included - allowed for unit connections > 4") | included | Upstream Dia (in) | 13.25 | Dwnstrm Dia (in) | 15.25 |  | 0.073981 | 0.22086 |  |  | 0.86885 | 26.025 |  |  |  | 0.035168 | 0.95754 | 11.6348 |  |  | 3/8, 40 ST | 0.493
Elbow Section (if included - allowed for unit connections > 4") | included | ID (inch) => | 13.25 | r/d or mitre=> | 2 x 45° mitre |  | 0.88593 | 2.6447 |  | 30 |  |  | 0.00013585 | 968145.2313 | 0.014038 | 0.42113 | 0.95754 | 11.6348 | Elbow Factors - | L/D | 1/2, 40 ST | 0.622
[19 empty] | r/d = 1 | 20 | 3/4, 40 ST | 0.824
Downstream Pipe, Water Temperature (F) | 44 | [7 empty] | 3.5101 | [9 empty] | r/d = 1.5 | 14 | 1, 40 ST | 1.049
Inside Diameter at Static Pressure Measurement Location (inches) | 13.25 | Length (of straight pipe) | 14 | (inches) |  |  | 0.031592 | 0.09431 |  |  |  |  | 0.00013585 | 822175.7075 | 0.014213 |  | 0.95754 | 11.6348 | r/d = 2 | 12 | 1 1/4, 40 ST | 1.38
Contraction or Enlargement Section (if included - allowed for unit connections > 4") | included | Upstream Dia (in) | 15.25 | Dwnstrm Dia (in) | 13.25 |  | 0.092876 | 0.27726 |  |  | 0.86885 | 26.025 |  |  |  | 0.077471 | 1.2684 | 8.7831 | r/d = 3 | 12 | 1 1/2, 40 ST | 1.61
Elbow Section (if included - allowed for unit connections > 4") | included | ID (inch) => | 13.25 | r/d or mitre=> | 2 x 45° mitre |  | 0.89698 | 2.6777 |  | 30 |  |  | 0.00013585 | 822175.7075 | 0.014213 | 0.42638 | 0.95754 | 11.6348 | r/d = 4 | 14 | 2, 40 ST | 2.067
[19 empty] | 2 x 45° mitre | 30 | 2 1/2, 40 ST | 2.469
[6 empty] | * Maximum Pressure Drop correction for the Evaporator (ft H2O) = | 2.0126 | 6.0081 | [10 empty] | 3 x 30° mitre | 24 | 3, 40 ST | 3.068
[19 empty] | 6 x 15° mitre | 24 | 4, 40 ST | 4.026
[21 empty] | 6, 40 ST | 6.065
Condenser Piping | [6 empty] | Press Drop Correction (ft) | Press Drop Correction (kPa) | dyn visc (lbm/ft/hr) | L/D | Dia Ratio | calc angle (deg) | Relative Roughness | Reynolds Nbr | Fric factor | K Factor | Area (ft2) | Velocity (ft/sec) |  |  | 8, 30 | 8.071
Upstream Pipe, Water Temperature (F) | 85 | Flow Rate (gpm) | 6000 | [5 empty] | 1.9184 | [11 empty] | 8, 40 ST | 7.981
Inside Diameter at Static Pressure Measurement Location (inches) | 13.25 | Length (of straight pipe) | 14 | (inches) |  |  | 0.043282 | 0.12921 |  |  |  |  | 0.00013585 | 1805170.4291 | 0.013522 |  | 0.95754 | 13.9617 |  |  | 10, 30 | 10.136
Contraction or Enlargement Section (if included - allowed for unit connections > 4") | included | Upstream Dia (in) | 13.25 | Dwnstrm Dia (in) | 15.25 |  | 0.10653 | 0.31803 |  |  | 0.86885 | 26.025 |  |  |  | 0.035168 | 0.95754 | 13.9617 |  |  | 10, 40 ST | 10.02
Elbow Section (if included - allowed for unit connections > 4") | included | ID (inch) => | 13.25 | r/d or mitre=> | 2 x 45° mitre |  | 1.2289 | 3.6686 |  | 30 |  |  | 0.00013585 | 1805170.4291 | 0.013522 | 0.40567 | 0.95754 | 13.9617 |  |  | 12, 30 | 12.09
[21 empty] | 12, ST | 12
Downstream Pipe, Water Temperature (F) | 95 | [7 empty] | 1.7073 | [11 empty] | 12, 40 | 11.938
Inside Diameter at Static Pressure Measurement Location (inches) | 13.25 | Length (of straight pipe) | 14 | (inches) |  |  | 0.043046 | 0.12851 |  |  |  |  | 0.00013585 | 2028358.3026 | 0.013449 |  | 0.95754 | 13.9617 |  |  | 14, 30 ST | 13.25
Contraction or Enlargement Section (if included - allowed for unit connections > 4") | included | Upstream Dia (in) | 15.25 | Dwnstrm Dia (in) | 13.25 |  | 0.13374 | 0.39926 |  |  | 0.86885 | 26.025 |  |  |  | 0.077471 | 1.2684 | 10.5398 |  |  | 14, 40 | 13.126
Elbow Section (if included - allowed for unit connections > 4") | included | ID (inch) => | 13.25 | r/d or mitre=> | 2 x 45° mitre |  | 1.2222 | 3.6486 |  | 30 |  |  | 0.00013585 | 2028358.3026 | 0.013449 | 0.40346 | 0.95754 | 13.9617 |  |  | 16, 30 ST | 15.25
[21 empty] | 18, ST | 17.25
[6 empty] | * Maximum Pressure Drop correction for the Condenser (ft H2O) = | 2.7777 | 8.2923 | [12 empty] | 18, 30 | 17.126
[21 empty] | 20, 20 ST | 19.25
|  | * Note: The pressure drop adjustment is limited to 10% of the pressure drop reading | [18 empty] | 20, 30 XS | 19
Notes:
1) Length (of straight pipe) - the straight pipe length of the flow tube section between the static pressure taps and the unit connection. Do not include any lengths associated with an elbow or expansion/contraction section.
2) r/d or mitre - The worksheet calculates an adjustment for various 90 degree elbow fittings. r/d = is the turn radius of the elbow divided by the inside diameter. Mitre type elbows are allowed for mitres <= 45 degrees.

## Pd Adjust (SI)
Water Pressure Drop Adjustment Calculations - ref: 551/591 appendix G
Evaporator Piping | [6 empty] | Press Drop Correction (kPa) | Convert data to IP |  |  | dyn visc (lbm/ft/hr) | L/D | Dia Ratio | calc angle (deg) | Relative Roughness | Reynolds Nbr | Fric factor | K Factor | Area (ft2) | Velocity (ft/sec) |  |  | Typical Steel Pipe Diameters (in)
Upstream Pipe, Water Temperature (C) | 12 | Flow Rate (l/s) | 60 |  |  |  |  | 53.6 | 951.0223 |  | 2.9999 | [11 empty] | Nominal Size/ Sched | ID
Flow Tube Inside Diameter at Static Pressure Measurement Location (mm) | 200 | Length (of straight pipe) | 800 | (mm) |  |  | 0.12017 | 7.874 | 31.4961 | [5 empty] | 0.0002286 | 307901.1634 | 0.01649 |  | 0.33816 | 6.2664 | Material Roughness (ft) | 0.00015 | 1/4, 40 ST | 0.364
Contraction or Enlargement Section (if included - allowed for unit connections > 100mm) | included | Upstream Dia (mm) | 200 | Dwnstrm Dia (mm) | 250 |  | 0.20183 |  | 7.874 | 9.8425 |  |  | 0.8 | 38.3898 |  |  |  | 0.11079 | 0.33816 | 6.2664 |  |  | 3/8, 40 ST | 0.493
Elbow Section (if included - allowed for unit connections > 100mm) | included | ID (mm) => | 200 | r/d or mitre=> | 2 x 45° mitre |  | 0.90124 |  | 7.874 |  |  | 30 |  |  | 0.0002286 | 307901.1634 | 0.01649 | 0.49471 | 0.33816 | 6.2664 | Elbow Factors - | L/D | 1/2, 40 ST | 0.622
[21 empty] | r/d = 1 | 20 | 3/4, 40 ST | 0.824
Downstream Pipe, Water Temperature (C) | 7 | [6 empty] | 44.6 |  |  | 3.4751 | [9 empty] | r/d = 1.5 | 14 | 1, 40 ST | 1.049
Inside Diameter at Static Pressure Measurement Location (mm) | 200 | Length (of straight pipe) | 800 | (mm) |  |  | 0.12208 | 7.874 | 31.4961 | [5 empty] | 0.0002286 | 265801.3271 | 0.016753 |  | 0.33816 | 6.2664 | r/d = 2 | 12 | 1 1/4, 40 ST | 1.38
Contraction or Enlargement Section (if included - allowed for unit connections > 100mm) | included | Upstream Dia (mm) | 250 | Dwnstrm Dia (mm) | 200 |  | 0.1725 |  | 9.8425 | 7.874 |  |  | 0.8 | 38.3898 |  |  |  | 0.23118 | 0.52837 | 4.0105 | r/d = 3 | 12 | 1 1/2, 40 ST | 1.61
Elbow Section (if included - allowed for unit connections > 100mm) | included | ID (mm) => | 200 | r/d or mitre=> | 2 x 45° mitre |  | 0.91559 |  | 7.874 |  |  | 30 |  |  | 0.0002286 | 265801.3271 | 0.016753 | 0.50259 | 0.33816 | 6.2664 | r/d = 4 | 14 | 2, 40 ST | 2.067
[21 empty] | 2 x 45° mitre | 30 | 2 1/2, 40 ST | 2.469
[6 empty] | * Maximum Pressure Drop correction for the Evaporator (kPa) = | 2.4334 | [13 empty] | 3 x 30° mitre | 24 | 3, 40 ST | 3.068
[21 empty] | 6 x 15° mitre | 24 | 4, 40 ST | 4.026
[23 empty] | 6, 40 ST | 6.065
Condenser Piping | [6 empty] | Press Drop Correction (ft) |  |  |  | dyn visc (lbm/ft/hr) | L/D | Dia Ratio | calc angle (deg) | Relative Roughness | Reynolds Nbr | Fric factor | K Factor | Area (ft2) | Velocity (ft/sec) |  |  | 8, 30 | 8.071
Upstream Pipe, Water Temperature (C) | 30 | Flow Rate (l/s) | 70 |  |  |  |  | 86 | 1109.5261 |  | 1.8951 | [11 empty] | 8, 40 ST | 7.981
Inside Diameter at Static Pressure Measurement Location (mm) | 200 | Length (of straight pipe) | 800 | (mm) |  |  | 0.1549 | 7.874 | 31.4961 | [5 empty] | 0.0002286 | 568640.6988 | 0.015617 |  | 0.33816 | 7.3108 |  |  | 10, 30 | 10.136
Contraction or Enlargement Section (if included - allowed for unit connections > 100mm) | included | Upstream Dia (mm) | 200 | Dwnstrm Dia (mm) | 250 |  | 0.27471 |  | 7.874 | 9.8425 |  |  | 0.8 | 38.3898 |  |  |  | 0.11079 | 0.33816 | 7.3108 |  |  | 10, 40 ST | 10.02
Elbow Section (if included - allowed for unit connections > 100mm) | included | ID (mm) => | 200 | r/d or mitre=> | 2 x 45° mitre |  | 1.1617 |  | 7.874 |  |  | 30 |  |  | 0.0002286 | 568640.6988 | 0.015617 | 0.46851 | 0.33816 | 7.3108 |  |  | 12, 30 | 12.09
[23 empty] | 12, ST | 12
Downstream Pipe, Water Temperature (F) | 35 | [6 empty] | 95 |  |  | 1.7073 | [11 empty] | 12, 40 | 11.938
Inside Diameter at Static Pressure Measurement Location (mm) | 200 | Length (of straight pipe) | 800 | (mm) |  |  | 0.15373 | 7.874 | 31.4961 | [5 empty] | 0.0002286 | 631176.0854 | 0.0155 |  | 0.33816 | 7.3108 |  |  | 14, 30 ST | 13.25
Contraction or Enlargement Section (if included - allowed for unit connections > 100mm) | included | Upstream Dia (mm) | 250 | Dwnstrm Dia (mm) | 200 |  | 0.23479 |  | 9.8425 | 7.874 |  |  | 0.8 | 38.3898 |  |  |  | 0.23118 | 0.52837 | 4.6789 |  |  | 14, 40 | 13.126
Elbow Section (if included - allowed for unit connections > 100mm) | included | ID (mm) => | 200 | r/d or mitre=> | 2 x 45° mitre |  | 1.153 |  | 7.874 |  |  | 30 |  |  | 0.0002286 | 631176.0854 | 0.0155 | 0.465 | 0.33816 | 7.3108 |  |  | 16, 30 ST | 15.25
[23 empty] | 18, ST | 17.25
[6 empty] | * Maximum Pressure Drop correction for the Condenser (kPa) = | 3.1329 | [15 empty] | 18, 30 | 17.126
[23 empty] | 20, 20 ST | 19.25
|  | * Note: The pressure drop adjustment is limited to 10% of the pressure drop reading | [20 empty] | 20, 30 XS | 19
Notes:
1) Length (of straight pipe) - the straight pipe length of the flow tube section between the static pressure taps and the unit connection. Do not include any lengths associated with an elbow or expansion/contraction section.
2) r/d or mitre - The worksheet calculates an adjustment for various 90 degree elbow fittings. r/d = is the turn radius of the elbow divided by the inside diameter. Mitre type elbows are allowed for mitres <= 45 degrees.