## Test Data to Standard (IP)
Enter the altitude of the test location - ZH |  |  |  | Procedure for Correcting Test Data to Standard Rating Condition Atmospheric Pressure
| ZH | 3500 | ft
Enter 100% Load Point test Capacity - Qtested |  |  |  |  | Table F1. Correction Factor (CF) Coefficients
| Qtested | 198.5 | tonR |  |  | Capacity DQ |  |  | Efficiency Dη
Enter 100% Load Point test efficiency - ηtested |  |  |  |  | Units of Measure for P | AQ | BQ | CQ | Aη | Bη | Cη
| ηtested / ƞtest,100% | 10.35 | EER |  | IP (psia) | 0.0011273 | -0.041272 | 1.363 | 0.0024308 | -0.090075 | 1.7987
Enter Part Load Point test Capacity - Qtest |  |  |  |  | Note: E indicates scientific notation, example: 1E-02 = 0.01
| Qtest | 160 | tonR
Enter Part Load Point test efficiency - ηtest |  |  |  |  | Capacity Correction Factor DQ |  |  | Efficiency Correction Factor - Dƞ
| ηtest | 12.6 | EER |  | DQ = AQ · p2 + BQ · p + CQ |  |  | Dƞ = Aƞ · p2 + Bƞ · p + Cƞ
[5 empty] | DQ = | 1.0179 |  | Dƞ = | 1.0404
[5 empty] | Atmospheric correction factor for capacity |  |  |  |  | Test results for net capacity, corrected to standard atmospheric pressure
Fixed values
| Parameter | Value | Units
| β | -0.00198 | K/ft |  | Atmospheric correction factor for efficiency |  |  |  |  | Test results for Efficiency (EER), corrected to standard atmospheric pressure
| ZH0 | 0 | ft
| g0 | 32.1741 | ft/s2
| M0 | 28.9644 | kg/kmol |  | exponent | -0.40901
| R* | 89494.5 | lb ft2 / (lb-mol K s2) |  | exp | 0.66431
| ρ0 | 14.696 | psia | !00% Load Point Calculations | [5 empty] | Part Load Point Calculations
| T0 | 288.15 | K |  |  | Correction factor CFq = | 1.0119 |  |  |  |  | Correction factor CFq = | 1.0096
Atmospheric pressure for the altitude entered | [5 empty] | Correction factor CFη = | 1.0269 |  |  |  |  | Correction factor CFη = | 1.0217
| g0·M0 / (β·R*) | -5.2591 |  |  |  | Corrected test capacity Qcorrected standard = | 200.9 | tonR |  |  |  | Corrected test capacity Qcorrected standard = | 161.9 | tonR
T0 /(T0+β*(ZH -Z0 )) |  | 1.0246 |  |  |  | Corrected test efficiency ηcorrected standard = | 10.63 | EER |  |  |  | Corrected test efficiency ηcorrected standard = | 12.87 | EER
0.87983
| P test | 12.93
Instructions for Use
Enter the test data into the yellow background cells,
Note on C2: Enter in location altitude
Note on C4: Enter the capacity from the test
Note on C6: Enter the efficiency determined by test
Note on C8: Enter the capacity from the part load test
Note on C10: Enter the efficiency determined by test

## Test Data to Standard (SI)
Enter the altitude of the test location - ZH |  |  |  | Procedure for Correcting Test Data to Standard Rating Condition Atmospheric Pressure
| ZH | 274 | m
Enter 100% Load Point test Capacity - Qtested |  |  |  |  | Table F1. Correction Factor (CF) Coefficients
| Qtested | 693.2 | kW |  |  | Capacity DQ |  |  | Efficiency Dη
Enter 100% Load Point test efficiency - ηtested |  |  |  |  | Units of Measure for P | AQ | BQ | CQ | Aη | Bη | Cη
| ηtested / ƞtest,100% | 3.021 | COPR |  | SI (kPa) | 2.3713e-05 | -0.005986 | 1.363 | 5.1135e-05 | -0.013064 | 1.7987
Enter Part Load Point test Capacity - Qtest |  |  |  |  | Note: E indicates scientific notation, example: 1E-02 = 0.01
| Qtest | 560 | kW
Enter Part Load Point test efficiency - ηtest |  |  |  |  | Capacity Correction Factor DQ |  |  | Efficiency Correction Factor - Dƞ
| ηtest | 3.686 | COPR |  | DQ = AQ · p2 + BQ · p + CQ |  |  | Dƞ = Aƞ · p2 + Bƞ · p + Cƞ
[5 empty] | DQ = | 1.004 |  | Dƞ = | 1.0093
[5 empty] | Atmospheric correction factor for capacity |  |  |  |  | Test results for net capacity, corrected to standard atmospheric pressure
Fixed values
| Parameter | Value | Units
| β | -0.0065 | K/m |  | Atmospheric correction factor for efficiency |  |  |  |  | Test results for Efficiency (EER), corrected to standard atmospheric pressure
| ZH0 | 0 | ft
| g0 | 9.8066 | m/s2
| M0 | 28.9644 | kg/kmol |  | exponent | -0.28144
| R* | 8314.32 | J/ (K*kmol) |  | exp | 0.7547
| ρ0 | 101.325 | kPa | !00% Load Point Calculations | [5 empty] | Part Load Point Calculations
| T0 | 288.15 | K |  |  | Correction factor CFq = | 1.0031 |  |  |  |  | Correction factor CFq = | 1.0025
Atmospheric pressure for the altitude entered | [5 empty] | Correction factor CFη = | 1.007 |  |  |  |  | Correction factor CFη = | 1.0057
| g0·M0 / (β·R*) | -5.2559 |  |  |  | Corrected test capacity Qcorrected standard = | 695.3 | tonR |  |  |  | Corrected test capacity Qcorrected standard = | 561.7 | tonR
T0 /(T0+β*(ZH -Z0 )) |  | 1.0062 |  |  |  | Corrected test efficiency ηcorrected standard = | 3.042 | EER |  |  |  | Corrected test efficiency ηcorrected standard = | 3.707 | EER
0.96794
| P test | 98.0764 | kPa
Instructions for Use
Enter the test data into the yellow background cells,
Note on C2: Enter in location altitude
Note on C4: Enter the capacity from the test
Note on C6: Enter the efficiency determined by test
Note on C8: Enter the capacity from the part load test
Note on C10: Enter the efficiency determined by test