## Form 410-5 IP Units
SUGGESTED FORM FOR RATING CALCULATION PROCEDURE FOR SENSIBLE HEAT AIR COILS (Imperial Units, IP) AHRI CERTIFICATION PROGRAM FOR FORCED-CIRCULATION AIR-COOLING AND AIR-HEATING COILS
Company | [9 empty] | Date
Solution Procedure Steps for Specific Coil Application |  |  |  | Coil Line: |  |  |  |  | Coil Type: |  | Choose
Coil Surface:
|  |  |  | GENERAL PROCEDURE | [8 empty] | Choose Calc Method
To Solve for Rows Deep (Nr) |  | To Solve for Capacity (qs) |  | General Procedure | Item No. | Item Abbr. | Item Description |  |  |  | Calculation Procedure | Dimensions, IP | Numerical Input and Formulas
Steam Coils | Hot or Cold Water Coils | Steam Coils | Hot or Cold Water Coils
1 | 1 | 1 | 1 | COIL PHYSICAL DATA | 1 | H | Coil Face Height |  |  |  |  | in
2 | 2 | 2 | 2 |  | 2 | L | Coil Face Length |  |  |  |  | in
3 | 3 | 3 | 3 |  | 3 | Af | Coil Face Area |  |  |  | Af = H * L/144 | ft2 | 0 | 0 | 0 | 0
4 | 4 | 4 | 4 |  | 4 | B | Surface Ratio (See Form 410-1)
|  | 5 | 5 |  | 5 | Nr | Coil Depth in Rows
|  | 6 | 6 |  | 6 | Nt | Total Number of Tubes in Coil
6 | 6 | 7 | 7 |  | 7 | Nc | Number of Tube Circuits in Coil
7 | 7 | 8 | 8 |  | 8 |  | Ao/(Af*Nr) |  |  |  |  | ft2/ft2F.A·row
|  | 9 | 9 |  | 9 | Ao | Total External Coil Surface |  |  |  | Ao = Ao/(Af*Nr)*Af*Nr | ft2 | 0 | 0 | 0 | 0
8 | 8 | 10 | 10 |  | 10 | Di | Tube Inside Diameter |  |  |  |  | in
9 | 9 | 11 | 11 |  | 11 | Aix | Total Cross-Sectional Fluid Flow Area |  |  |  | Aix = π/4*(Di/12)2*Nc | ft2 | 0 | 0 | 0 | 0
10 | 10 | 12 | 12 |  | 12 | Ls | Straight Tube Length per Tube Pass |  |  |  |  | in
| 11 |  | 13 |  | 13 | Ls/Di | Straight Tube Length per Pass/Tube Diameter | [5 empty] | 0 | 0 | 0 | 0
11 | 12 | 13 | 14 |  | 14 | Kb | Equivalent Length of Coil Circuit per Return Bend |  |  |  |  | in
12 | 13 | 14 | 15 |  | 15 | Le | Total Equivalent Length of Coil Circuit |  |  |  | Le=(1/12)*[Ls*(Nt/Nc)+ Kb*(Nt/Nc-1)] | ft | 0 | 0 | 0 | 0
13 | 14 | 15 | 16 | RATING CONDITIONS | 16 | cp | Specific heat of air-water vapor mixture To simplify calculation and rating procedures, a constant value of 0.243 may be used for cooling calculations and a constant value of 0.241 may be used for heating calculations |  |  |  |  | Btu/lb·°F
14 | 15 | 16 | 17 |  | 17 | QaSTD | Air Volume Flow at Standard Conditions |  |  |  |  | scfm
15 | 16 | 17 | 18 |  | 18 | Va | Standard Air Face Velocity |  |  |  | Va = QaSTD/Af | ft/min | 0 | 0 | 0 | 0
16 | 17 | 18 | 19 |  | 19 | t1db | Entering Air Dry-Bulb Temperature |  |  |  |  | °F
| 18 |  | 20 |  | 20 | Vw | Avg. Standard Water Velocity |  |  |  |  | ft/s
| 19 |  | 21 |  | 21 | tw1 | Entering Water Temperature |  |  |  |  | °F
17 | 20 | 19 | 22 |  | 22 | Ps | Avg. Absolute Static Pressure at Coil |  |  |  |  | in Hg abs
18 |  | 20 |  |  | 23 | Pv1 | Inlet Steam Gauge Pressure to Coil |  |  |  |  | psig
19 |  | 21 |  |  | 24 | tv1 | Inlet Steam Temperature to Coil |  |  |  |  | °F
20 |  | 22 |  |  | 25 | Pv1 | Coil Inlet Steam Pressure |  |  |  | Pv1 = Pv1(gauge) + 14.696/29.921*Ps | psia | 0 | 0 | 0 | 0
21 |  | 23 |  |  | 26 | tv1g | Steam Saturation Temperature Entering Coil From Pv1 and Steam Property Tables |  |  |  |  | °F
22 | 21 |  |  |  | 27 | qs | Coil Sensible Heat (Known when solving for rows deep) |  |  |  |  | Btu/h
23 | 22 | 24 | 23 |  | 28 | Δto | Initial Air-to-Fluid Temperature Difference |  |  |  |  | °F
[8 empty] | Single Tube Steam |  |  | = tv1g - t1db
[8 empty] | Hot Water |  |  | = tw1 - t1db
[8 empty] | Cold Water |  |  | = t1db - tw1
24 |  | 25 |  | STEAM PROPERTIES | 29 | vv1 | vv1 Steam Specific Volume Entering Coil (From tv1g, Pv1 and Steam Property Tables) = vv2 = vvmg for rating convenience |  |  |  |  | ft3/lb
25 |  | 26 |  |  | 30 | hv1 | Enthalpy of Steam Entering Coil From tv1, Pv1, and Steam Property Tables |  |  |  |  | Btu/lb
26 |  | 27 |  |  | 31 | hf2 | Enthalpy of Steam Condensed Leaving Coil From Pv1 and Steam Tables assuming hf1 = hf2 for rating convenience |  |  |  |  | Btu/lb
| 23 |  | 24 |  | 32 | ww | Water Flow Rate |  |  |  | ww = 62.361*3600*(Aix*Vw) | lb / hr | 0 | 0 | 0 | 0
| 24 |  |  |  | 33 | Δtw | Water Temperature Rise or Drop Across Coil |  |  |  | Δtw = qs/ww | °F | 0 | 0 | 0 | 0
| 25 |  | 25 |  | 34 | twm | Average Water Temperature Inside Tubes When solving for rows deep = tw1 - (0.5*Δtw) For Air-Heating Coil = tw1 + (0.5*Δtw) For Air-Cooling Coil When solving for capacity, this value must be approximated. (Suggest twm be 5°F to 10°F from tw1) |  |  |  |  | °F
| 26 |  | 26 |  | 35 | ρw | Density of Water at Mean Water Temp., twm |  |  |  |  | lb/ft3
| 27 |  | 27 |  | 36 | cpw | Specific Heat of Water at Mean Water Temp., twm |  |  |  |  | Btu/lb·°F
| 28 |  | 28 |  | 37 | μw | Dynamic Viscosity of Water at Mean Water Temp., twm |  |  |  |  | lb/ft·h
| 29 |  | 29 |  | 38 | kw | Thermal Conductivity of Water at Mean Water Temp., twm |  |  |  |  | Btu·ft/ h·ft2·°F
| 30 |  | 30 |  | 39 | Prw | Prandtl Number of Water at Mean Water Temp, twm |  |  |  | cpw*μw/kw | - | 0 | 0 | 0 | 0
| 31 |  | 31 |  | 40 | Prw2/3 |  |  |  |  | (cpw*μw/kw)2/3 | - | 0 | 0 | 0 | 0
| 32 |  | 32 |  | 41 | Gw | Mass Velocity of Water at Mean Water Temp., twm |  |  |  | ww/Aix | lb/h·ft2 | 0 | 0 | 0 | 0
| 33 |  | 33 |  | 42 | Rew | Reynolds Number of Water at Mean Water Temp., twm |  |  |  | Rew = Gw*Di/(12*μw) | - | 0 | 0 | 0 | 0
| 34 |  | 34 |  | 43 | jw | Colburn j Factor from Fig. 17 with Rew and Ls/Di |  |  |  |  | -
| 35 |  | 35 |  | 44 | (μtw/μw).14 init | Initial Estimate Dynamic Viscosity Ratio (VRinit) For Air-Cooling Water Coils use initial estimate of 0.98 and for Air-Heating Water Coils use initial estimate of 1.03
| 36 |  | 36 |  | 45 | fw | Initial Estimate of Water Side Film Heat Transfer Coefficient |  |  |  | jw*cpw*Gw/(Prw2/3*μtw/μw0.14) |  | 0 | 0 | 0 | 0
| 37 |  | 37 |  | 46 | Rffa | Fouling Factor Allowance for Water (assumed to be zero unless otherwise specified) |  |  |  |  | h·ft2·°F/Btu | 0 | 0 | 0 | 0
| 38 |  | 38 |  | 47 | Rw | Initial Estimate of Water Film Thermal Resistance |  |  |  | = B(1/fw + Rffa) | h·ft2·°F/Btu | 0 | 0 | 0 | 0
| 39 |  | 39 |  | 48 | RaD+ RmD | Combined Air Film plus Metal Thermal Resistance (From Fig. 16 with Va) |  |  |  |  | h·ft2·°F/Btu
| 40 |  | 40 |  | 49 | R | Overall Thermal Resistance between Air and Tube Side Fluid |  |  |  |  | h·ft2·°F/Btu | 0 | 0 | 0 | 0
[7 empty] | R = Rw + (RaD+RmD) for Hot Water and Cold Water Coils |  |  |  |  | h·ft2·°F/Btu | 0 | 0 | 0 | 0
27 |  | 28 |  |  |  |  | From Fig. 15 knowing Va for Single Tube Steam Coils |  |  |  |  | h·ft2·°F/Btu
|  | 29 | 41 |  | 50 | co | Heat Transfer Exponent (Air-to-Fluid) |  |  |  | co = Ao/(4.5*cp*QaSTD*R) |  | 0 | 0 | 0 | 0
28 | 41 | 30 | 42 |  | 51 | M | Air-to-Fluid-Side Heat Capacity Ratio Note: M=0 for Steam Coils(for rating convenience)
[8 empty] | Single Tube Steam |  |  | M = 0 (for rating convenience) |  | 0 | 0 | 0 | 0
[8 empty] | Water Coils |  |  | M = (4.5*cp*QaSTD)/ww for Water |  | 0 | 0 | 0 | 0
|  | 31 | 43 |  | 52 | E | Air-Side From Section 6.5
|  | 32 | 44 |  | 53 | qs | Coil Sensible Heat |  |  |  | qs = 4.5*cp*QaSTD*E*Δto | Btu/h | 0 | 0 | 0 | 0
|  |  | 45 |  | 54 | Δtw | Water Temperature Rise or Drop Across Coil |  |  |  | Δtw = qs/ww | °F | 0 | 0 | 0 | 0
|  |  | 46 | CALCULATIONS TO SOLVE FOR ROWS DEEP | 55 | *twm | Average Water Temperature Inside Tubes = tw1 - (0.5*Δtw) For Air-Heating Coil = tw1 + (0.5*Δtw) For Air-Cooling Coil * If within +/- 3 °F of Item 34, proceed to next step. If not, assume a new value for Item 34 and repeat calculations through Item 54 |  |  |  |  | °F | 0 | 0 | 0 | 0
29 | 42 | 33 | 47 |  | 56 | Δtadb | Air Temperature Rise or Drop Across Coil |  |  |  | Δtadb = qs/(4.5*cp*QaSTD) | °F | 0 | 0 | 0 | 0
30 | 43 |  |  |  | 57 | E | Air-Side Effectiveness |  |  |  | E = Δtadb/Δto |  | 0 | 0 | 0 | 0
31 | 44 |  |  |  | 58 | co | Heat Transfer Exponent (Air-to-Fluid) From Section 6.5 |  |  |  | For Steam co = -ln (1 - e)
| 45 |  | 48 |  | 59 | MTD | Mean Temperature Difference |  |  |  | MTD = Δtadb/co | °F
| 46 |  | 49 |  | 60 | ttwm | Estimate of Mean Tube Wall Temperature |  |  |  | ttwm = twm +/- (Rw/R)*MTD | °F | 0 | 0 | 0 | 0
| 47 |  | 50 |  | 61 | μtwm | Dynamic Viscosity of Water at Tube Wall Temp., ttwm |  |  |  |  | lb/ft·h
| 48 |  | 51 |  | 62 | (μtw/μw).14 calc | Calculated Dynamic Viscosity Ratio (VRcalc) If VRinit is not within 2 % of VRcalc , use VRcalc as new VRinit and recalculate starting with Item 44. Otherwise, proceed to next step | [5 empty] | 0 | 0 | 0 | 0
32 | 49 | 34 | 52 |  | 63 | t2db | Leaving Air Temperature at Coil |  |  |  |  | °F | 0 | 0 | 0 | 0
[7 empty] | t2db = t1db + Δtadb For Air Heating | [5 empty] | 0 | 0 | 0 | 0
[7 empty] | t2db = t1db - Δtadb For Air Cooling | [5 empty] | 0 | 0 | 0 | 0
| 50 |  | 53 |  | 64 | tw2 | Leaving Water Temperature at Coil |  |  |  |  | °F | 0 | 0 | 0 | 0
[8 empty] | = tw1 - Δtw For Air Heating Coil |  |  |  |  | 0 | 0 | 0 | 0
[8 empty] | = tw1 + Δtw For Air Cooling Coil |  |  |  |  | 0 | 0 | 0 | 0
33 | 51 |  |  |  | 65 | Nrc | Calculated Row Depth Required |  |  |  | Nrc = (qs*R*co) /((Ao/Af*Nr)*Af*Δtadb) |  | 0 | 0 | 0 | 0
34 | 52 |  |  | AIR-SIDE PRESS DROP | 66 | Nr | Integral Coil Row Depth Installed
35 | 53 | 35 | 54 |  | 67 | ΔPst /Nr | Air-Side Pressure Drop Per Row Deep at Standard Conditions (From Fig. 15 or 16 with Va) |  |  |  |  | in H20 /row
36 | 54 | 36 | 55 |  | 68 | Fa | Air-Side Pressure Drop Correction Factor |  |  |  | Fa=(460+((t1db +t2db)/2))/(Ps*530/29.921) |  | 0 | 0 | 0 | 0
37 | 55 | 37 | 56 |  | 69 | (ΔPst)JOB | Air-Side Pressure Drop at Job Conditions |  |  |  | (For constant wa) (∆Pst) JOB = Nr*(ΔPst /Nr)*Fa |  | 0 | 0 | 0 | 0
38 |  | 38 |  | TUBE-SIDE PRESSURE DROP CALCULATIONS | 70 | wv | Total Steam Condensate Mass Flow Rate Through Coil |  |  |  | wv = (qs)/(hv1-hf2) | lb/h | 0 | 0 | 0 | 0
39 |  | 39 |  |  | 71 | wv/Nc | Steam Flow Rate per Tube Circuit |  |  |  | Eq. = wv/Nc | lb/h | 0 | 0 | 0 | 0
[5 empty] | 72 |  | Obtain Header, Nozzle and Entrance and Exit Losses for Water and Steam (to be determined by manufacturer)
| 56 |  | 57 |  |  | hLhca/Fh | for Water Coils at Mean Water Temp with Vw> |  |  |  | For hdr/conn/assy hLhca/Fh | ft H20
42 |  | 40 |  |  |  | ΔPhca/vvmg | for Steam Coils -> |  |  |  | ΔPhca/vvmg | lb2/ in2·ft3
| 57 |  | 58 |  | 73 |  | ΔPt/LeFt - Tube Circuit Water Pressure Drop Parameter at Mean Water Temp (From Fig. 16 with Vw) (Ft = 1) |  |  |  |  | ft H20 /ft
| 58 |  | 59 |  | 76 | (ΔPw)JOB | Water Pressure Drop Across Coil at Job Conditions |  |  |  | (ΔPw)JOB = hLhca + Le*(ΔPt/Le) | ft H20 | 0 | 0 | 0 | 0
43 |  | 41 |  |  | 77 |  | ΔPtv/Levvm - Steam Pressure Drop Parameter (From Fig. 15 with wv/Nc) |  |  |  |  | lb2/ in2·ft3
44 |  | 42 |  |  | 78 | ΔPv | Steam Pressure Drop Inside Tubes at Job Conditions |  |  |  | ΔPv=((ΔPtv/Levvm*Le)+(ΔPhca/vvmg))*vv1 | psi | 0 | 0 | 0 | 0