## Form 410-7 IP Units
CALCULATION OF HEAT TRANSFER COEFFICIENT AND FRICTION FACTOR FOR GLYCOL COILS (Imperial Units, IP) AHRI CERTIFICATION PROGRAM FOR FORCED-CIRCULATION AIR-COOLING AND AIR-HEATING COILS
Company: |  |  |  |  | Date:
General Category | Item Number | Abbreviation | General Description | Calculation Procedure |  | Dimensions, IP | Numerical Input and Formulas
COIL PHYSICAL DATA | 1 | Ao | Total External Coil Surface (From Form 410-1) |  |  | ft.2
| 2 | Di | Tube Inside Diameter (From Form 410-1) |  |  | in.
| 3 | Nt | Total Number of Tubes in Coil |  |  | --
| 4 | Lt | Fin Tube Length |  |  | in.
| 5 | B | Surface Ratio (From Form 410-1) |  |  | IP
| 6 | Nc | Number of Tube Circuits in Coil |  |  | --
| 7 | Aix | Total Cross-Sectional Fluid Flow Area | Aix, IP = 0.00545*Di2*Nc |  | ft.2 | 0
| 8 | Ls | Straight Tube Length per Tube Pass |  |  | in.
| 9 | Kb | Equivalent Length of Coil Circuit per Return Bend |  |  | in.
| 10 | Le | Total Equivalent Length of Coil Circuit | Le, IP=0.0833*[Ls*(Nt/Nc)+ Kb*(Nt/Nc-1)] |  | ft. | #DIV/0!
TEST RUN NUMBER
[7 empty] | 1 | 2 | 3 | 4
OBSERVATIONS AND CALCULATIONS | 11 | Ps | Average Absolute Static Pressure at Coil |  |  | in. Hg abs
| 12 | t1 | Entering Air Dry-Bulb Temperature |  |  | °F
| 13 | t'1 | Entering Air Wet-bulb Temperature |  |  | °F
| 14 | h1 | Entering Air Enthalpy |  |  | Btu/lb
| 15 | t2 | Leaving Air Dry-Bulb Temperature |  |  | °F
| 16 |  | Glycol Concentration |  |  | --
| 17 | Va | Standard Air Face Velocity |  |  | ft/min
| 18 | tg1 | Entering Glycol Temperature |  |  | °F
| 19 | tg2 | Leaving Glycol Temperature |  |  | °F
| 20 | tgm | Mean Glycol Temperature | tgm = 0.5*(tg1+tg2) |  | °F | 0 | 0 | 0 | 0
| 21 | wg | Glycol Flow Rate |  |  | lb/hr
CALCULATIONS OF GLYCOL THERMAL RESISTANCE | 22 | qs | Average Sensible Cooling Capacity |  |  | Btuh
| 23 | Δtm | Overall Logarithmic Mean Temperature Difference (If other than thermal counter flow, determine the logarithmic mean temperature difference from Section 6.5) | Δtm = ((t1-tg2)-(t2-tg1)) / (ln((t1-tg2)/(t2-tg2))) |  | °F | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| 24 | R | Overall Thermal Resistance | R = A0*Δtm / qs |  | hr*ft2*F /Btu | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| 25 | RaD+ RmD | Combines Air Film plus Metal Thermal Resistance (From Fig. 16 with Va) |  |  | hr*ft2*F /Btu
| 26 | Rg | Film Thermal Resistance of Glycol | Rg = R-(RaD+ RmD) |  | hr*ft2*F /Btu | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| 27 | fg | Glycol Film Heat Transfer Coefficient | fg = B-Rg |  | Btu/ hr*ft2*F | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| 28 | ttw | Average Tube Wall Temperature | ttw = tgm+(Rg/R)*Δtm |  | °F | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| 29 | μtw | Absolute Viscosity of Glycol at [16] and ttw |  |  | lb/ ft.*hr
| 30 | μg | Absolute Viscosity of Glycol at [16] and tgm |  |  | lb/ ft.*hr
| 31 | dg | Specific Gravity of Glycol at [16] and tgm |  |  | --
| 32 | cpg | Specific Heat of Glycol at [16] and tgm |  |  | Btu/ lb*°F
| 33 | kg | Thermal Conductivity of Glycol at [16] and tgm |  |  | Btu/ hr*ft2*F
| 34 |  | (μtw/μg)0.14 -Viscosity Ratio | (μtw/μg)0.14 |  | -- | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| 35 | Pr | Prandtl Number | Pr = (cpg*μg)/kg |  | -- | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| 36 | Pr(2/3) |  | Pr(2/3) |  | -- | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| 37 | Cg | Mass Velocity of Glycol | Cg = wg/Aix |  | lb/ ft.2*hr | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| 38 | vg | Kinematic Velocity of Glycol | vg, IP = μg/(224500*dg) |  | ft.2/s | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| 39 | j | Colburn Heat Transfer Factor for Glycol | j = (fg/(cpg*Cg))*(Pr(2/3)*[34]) |  | -- | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| 40 | Vg | Glycol Velocity Inside Tubes | Vg, IP = Cg/(224500*dg) |  | ft/s | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| 41 | Re | Reynolds Number for Glycol | Re, IP = (Vg*Di)/(12*vg) |  | -- | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| 42 | Δpg | Glycol Pressure Drop |  |  | ft. of Glyc
| 43 | Δph | Header and Tube Entrance and Exit Loss -Established by the manufacturer |  |  | ft. of Glyc
| 44 | Δpt /Le | Glycol Pressure Drop Inside Tubes | (Δpg-Δph)/Le |  | ft. Gly/ ft. tube | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| 45 | f' | Friction Factor for Glycol | f', IP = (1.34*Di*[44])/((Vg2)*[34]) |  | -- | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| 46 |  | Plot j vs Re on Logarithmic Coordinates as shown in Fig. 3 |  |  | -- | -- | -- | -- | --
| 47 |  | Plot f' vs Re on Logarithmic Coordinates as shown in Fig. 3 |  |  | -- | -- | -- | -- | --