## Form 410-9 IP Units
SUGGESTED FORM FOR RATING CALCULATION PROCEDURE FOR COOLING AND DEHUMIDIFYING COILS, WITH ETHYLENE (Imperial Units, IP) AHRI CERTIFICATION PROGRAM FOR FORCED-CIRCULATION AIR-COOLING AND AIR-HEATING COILS
Company | [6 empty] | Date
Solution Procedure Steps for Specific Coil Application |  | Coil Line: |  |  |  | Coil Type: |  |  |  | Numerical Input and Formulas
Coil Surface:
GENERAL PROCEDURE
Partially Wet Surface | Fully Wet Surface | General Procedure | Item No. | Item Abbr. | Item Description |  |  | Calculation Procedure | Dimensions, IP
-- | -- |  | -- | cpg | Specific Heat of Gas at Constant Pressure |  |  |  | Btu /lb*°F
1 | 1 | COIL PHYSICAL DATA | 1 | H | Coil Face Height |  |  |  | in.
2 | 2 |  | 2 | L | Coil Face Length |  |  |  | in.
3 | 3 |  | 3 | Af | Coil Face Area |  |  |  | ft2
4 | 4 |  | 4 | B | Surface Ratio (See Form 410-1) |  |  |  | --
5 | 5 |  | 5 | Nr | Coil Depth in Rows (if known) |  |  |  | --
6 | 6 |  | 6 | Nt | Total Number of Tubes in Coil (if known) |  |  |  | --
7 | 7 |  | 7 | Nc | Number of Tube Circuits in Coil (if known) |  |  |  | --
8 | 8 |  | 8 |  | Ao/Af*Nr |  |  |  | ft2/ ft2-F.A.
9 | 9 |  | 9 | Di | Tube Inside Diameter |  |  |  | in.
10 | 10 |  | 10 | Ls | Straight Tube Length per Tube Pass |  |  |  | in.
11 | 11 |  | 11 | Kb | Equivalent Length of Coil Circuit per Return Bend |  |  |  | in.
12 | 12 |  | 12 | Ao | Total External Coil Surface |  |  | Ao = [8]*Af*Nr | ft.2 | 0
13 | 13 |  | 13 | Aix | Total Cross-Sectional Fluid Flow Area, Inside Tubes |  |  | Aix, IP = 0.00545*Di2*Nc | ft.2 | 0
14 | 14 |  | 14 | Le | Total Equivalent Length of Coil Circuit |  |  | Le, IP = 0.0833*[Ls*(Nt/Nc) +Kb*(Nt/Nc-1)] | ft. | #DIV/0!
15 | 15 |  | 15 | Ls/Di | Ratio of Tube Length to Diameter |  |  | Ls /Di | -- | #DIV/0!
16 | 16 | RATING CONDITIONS & DATA COMPUTATION | 16 | Qa | Air Volume Flow at Standard Conditions |  |  |  | scfm
17 | 17 |  | 17 | Va | Standard Air Face Velocity |  |  | Va, IP = Qa/Af | ft/min | #DIV/0!
18 | 18 |  | 18 | t1 | Entering Air Dry-Bulb Temperature |  |  |  | °F
19 | 19 |  | 19 | t'1 | Entering Air Wet-bulb Temperature |  |  |  | °F
20 | 20 |  | 20 | wg | Total Ethylene Glycol Solution Flow Rate |  |  |  | lb per hr
21 | 21 |  | 21 | tg1 | Entering Ethylene Glycol Solution Temperature |  |  |  | °F
22 | 22 |  | 22 | Ps | Average Absolute Static Pressure at Coil |  |  |  | in. Hg abs
23 | 23 |  | 23 | h1 | Entering Air Enthalpy (From t1, t'1, and Ps) |  |  |  | Btu/lb
24 | 24 |  | 24 | wg /Nc | Ethylene Glycol Solution Flow Rate per Circuit |  |  | wg/Nc | lb / hr circuit | #DIV/0!
25 | 25 | RATING CONDITIONS, PARAMETERS, AND DATA COMPUTATIONS | 25 | t"1 | Entering Air Dew Point Temperature From Psychrometric Chart with Ps, t1, and t'1 |  |  |  | °F
[5 empty] | Note: Calculation of Dew Point Temp for Non-Standard Air Pressure* |  |  |  | --
[5 empty] | Pv, IP = p'-[((ps-p')*(t1-t'1))/(2830-(1.44*t'1))] |  |  |  | --
[5 empty] | Where: p' = Saturation Vapor Press. at t'1 from steam tables. Pv = Saturation Vapor Pressure at Dew Point Temp. |  |  |  | --
[5 empty] | Note: t"1 = Dew Point Temp. is Saturation Temp. Corresponding to Saturation Vapor Pressure, pv, from Steam Tables. |  |  |  | --
26 | 26 |  | 26 | h"1 | Saturation Enthalpy at Dew Point (From psychrometric charts with t"1 and Ps) |  |  |  | Btu/lb
27 | 27 |  | 27 | RaD | Air Film Thermal Resistance for Dry Surface (From Fig. 17 or 18 with Va) |  |  |  | hr*ft2*F /Btu
28 | 28 |  | 28 | RaW | Air Film Thermal Resistance for Wet Surface (From Fig. 17 or 18 with Va) |  |  |  | hr*ft2*F /Btu
29 | 29 |  | 29 | RmD | Metal Thermal Resistance for Dry Surface (From Fig. 14 with fa = 1/RaD) |  |  |  | hr*ft2*F /Btu
30 | 30 |  | 30 |  | Ethylene Glycol Concentration |  |  |  | % by wt
31 | 31 |  | 31 | 60wa | Standard Air Flow Rate |  |  | 60wa, IP = 4.50*Qa | lb/hr | 0
32 | 32 |  | 32 |  | Case I - If t'2 is known, determine h2 at t'2 saturated and Ps. Then calculate qt = 60wa(h1-h2)
Case II - If qt is known, determine h2 and then t'2. h2 = h1-(qt/60wa)
Case III - If Nr is known, assume h2 or t'2, find h2 and then t'2 or qt, respectively.
33 | 33 |  | 33 | t'2 | Leaving Air Wet-Bulb Temperature |  |  |  | °F
34 | 34 |  | 34 | h2 | Leaving Air Enthalpy If qt is known, h2 = h1-(qt/60wa) |  |  |  | Btu/lb
35 | 35 |  | 35 | qt | Total Heat Capacity of Coil (Enter numerical value if known. If not known, assume a numerical value for a trial and error solution.) |  |  | qt = 60wa*(h1-h2) | Btuh | 0
36 | 36 |  | 36 | tgm | Mean Ethylene Glycol Solution Temperature - When solving for rows deep this value must be calculated by trial and error using [26] and determining cpg for various values of tgm with the following equations: |  |  | tgm = tg1 + qt/(2*wg*cpg) | °F | #DIV/0!
37 | 37 |  | 37 | cpg | Specific Heat of Ethylene Glycol Solution at [26] & tgm |  |  |  | Btu /lb*°F
38 | 38 |  | 38 | dg | Specific Gravity of Ethylene Glycol Solution at [26] & tgm |  |  |  | --
39 | 39 |  | 39 | kg | Thermal Conductivity of Ethylene Glycol Solution at [26] & tgm |  |  |  | Btu/ hr *ft*°F
40 | 40 |  | 40 | μg | Absolute Viscosity of Ethylene Glycol Solution at [26] and tgm (Solution at [26] & [27] = centipoises x 2.42) |  |  |  | lb/ ft*hr
41 | 41 |  | 41 | νg | Kinematic Viscosity of Ethylene Glycol Solution |  |  | νg, IP = μg/(224500*dg) | ft.2/s | #DIV/0!
42 | 42 |  | 42 | Cg | Mass Velocity of Glycol |  |  | Cg = wg/Aix | lb /ft.2*hr | #DIV/0!
43 | 43 |  | 43 | Vg | Ethylene Glycol Solution Velocity Inside Tubes |  |  | Vg, IP = Cg/(224500*dg) | ft./s | #DIV/0!
44 | 44 |  | 44 | Re | Reynolds Number for Ethylene Glycol Solution |  |  | Re, IP = (Vg*Di)/(12*νg) | -- | #DIV/0!
45 | 45 |  | 45 | Pr | Prandtl Number for Ethylene Glycol Solution |  |  | Pr = cpg*μg/kg | -- | #DIV/0!
46 | 46 |  | 46 | Pr(2/3) |  |  |  | Pr(2/3) | -- | #DIV/0!
47 | 47 |  | 47 | j | Colburn Heat Transfer Factor for Ethylene Glycol Solution at Re, [14] and Fig. 3 |  |  |  | --
48 | 48 |  | 48 | tg2 | Leaving Ethylene Glycol Temperature |  |  | tg2 = (tg1+qt)/(wg*cpg) | °F | #DIV/0!
49 | 49 |  | 49 | Y | Ratio of Tube-Side Temperature Difference to Air Enthalpy Difference |  |  | Y = (tg1-tg2)/(h1-h2) | lb*°F /Btu | #DIV/0!
50 | 50 |  | 50 | ttw | Average Tube Wall Temperature (Approximate when solving for rows deep or capacity) Assume 10°F (5.6°C) to 15°F (8.3°C) from tgm |  |  |  | °F
51 | 51 |  | 51 | μtw | Absolute Viscosity of Ethylene Glycol Solution at [26] and ttw |  |  |  | lb /ft.*hr
52 | 52 |  | 52 | (μtw/ μg)0.14 | Viscosity Ratio |  |  | (μtw/ μg)0.14 | -- | #DIV/0!
53 | 53 |  | 53 | fg | Ethylene Glycol Solution Film Heat Transfer Coefficient |  |  | fg = (cpg*Cg*j)/((Pr(2/3))*[52]) | Btu/ hr *ft2*°F | #DIV/0!
54 | 54 |  | 54 | Rg | Film Thermal Resistance of Ethylene Glycol Solution |  |  | Rg = B/fg | hr*ft2*F /Btu | #DIV/0!
55 | 55 |  | 55 |  | Approximate Coil Characteristic |  |  | (Rg+RmD)/(0.243*RaW) | lb*°F /Btu | #DIV/0!
56 | 56 |  | 56 |  | Approximate Air Enthalpy at Boundary Conditions If [56]>h1 use [56]=h1 since coil is fully wet. |  |  | (t"1-tg2+(Y*h1)+([55]*h"1))/(Y+[55]) | Btu/lb | #DIV/0!
57 | 57 |  | 57 |  | Approximate Tube-Side Temperature at Dry-Wet Boundary |  |  | tg2-Y*(h1-[56]) | °F | #DIV/0!
58 | 58 |  | 58 |  | Mean Tube-Side Temperature
[6 empty] | For Partially Dry Coil |  | 0.5*(tg1+[57]) | °F | #DIV/0!
[6 empty] | For Fully-Wet Coil |  | 0.5*(tg1+tg2) | °F | #DIV/0!
59 | 59 |  | 59 |  | Approximate Mean Air Enthalpy of Wetted Section |  |  |  | -- | --
[6 empty] | For Partially Dry Coil |  | 0.5*([56]+h2) | Btu/lb | #DIV/0!
[6 empty] | For Fully-Wet Coil |  | 0.5*(h1+h2) | Btu/lb | 0
60 | 60 |  | 60 |  | Appx. Mean Surface Temp. for Fully Wet Coil or Wet Portion of Partially Dry Coil (With [52], [58] and [59]) |  |  |  | °F
61 | 61 |  | 61 | m"/ cp | Air-Side Heat Transfer Multiplier for Wet Coil or Wet Portion of Partially Dry Coil (From Equation 44 with [60], and Ps) |  |  |  | --
62 | 62 |  | 62 | faW | Air-Side Thermal Conductance for Wet Surface |  |  | faW = [61]/[RaW] | Btu/ hr*ft2*F | #DIV/0!
63 | 63 |  | 63 | RmW | Metal Thermal Resistance for Wet Surface (From Fig. 24 with faW) |  |  |  | hr*ft2*F /Btu
64 | 64 |  | 64 | C | Coil Characteristics for Wetted Surface *The appx value of C is used only to obtain the final value of RmW |  |  | C, IP = (Rg+RmW)/(0.243*RaW) | lb*°F /Btu | #DIV/0!
65 | 65 |  | 65 | hB | Air Enthalpy at Boundary If hB<h1, surface is partially dry, proceed to [66] If hB≥h1, surface is fully wet, proceed to [71] |  |  | (t"1-tg2+(Y*h1)+([64]*h"1))/(Y+[64]) | Btu/lb | #DIV/0!
66 | 66 |  | 66 | hm | Mean Air Enthalpy For a partially dry coil: If hm≥hB complete items [67] & [68]. If hm<hB, complete items [69], [70] & [71]. For a fully wet coil, complete items [69], [70] & [71]. (See figures on last page of this form) |  |  | 0.5*(h1+h2) | Btu/lb | 0
67 | -- |  | 67 | tm | Air Dry-Bulb Temperature where Tube-Side Temperature Equals tgm |  |  | tm, IP = tg2-((0.5*qt) /(0.243*60wa)) | °F | #DIV/0!
68 | -- |  | 68 | *ttw | Average Tube Wall Temperature |  |  | *ttw= tgm+(Rg*(tm-tgm)) /(RaD+RmD+Rg) | °F | #DIV/0!
69 | 67 |  | 69 | tsm | Surface Temp. Where Tube-Side Temperature Equals tgm (With Ps, tgm, C and hm) |  |  |  | °F
70 | 68 |  | 70 | hsm | Enthalpy of Saturated Air at tsm and Ps |  |  |  | Btu/lb
71 | 69 |  | 71 | *ttw | Average Tube Wall Temperature |  |  | *ttw= tgm+(Rg*(hm-hsm)) /(0.243*Raw) | °F | #DIV/0!
72 | -- |  | 72 | qtD | Capacity for Dry Portion of Coil |  |  | qtD = 60wa*(h1-hB) | Btuh | #DIV/0!
73 | -- |  | 73 | tB | Air Dry-Bulb Temperature at Boundary |  |  | tB, IP = t1-(qtD/(0.243*60wa)) | °F | #DIV/0!
74 | -- |  | 74 | tgB | Tube Side Temperature at Boundary |  |  | tgB = tg2-Y*(h1-hB) | °F | #DIV/0!
75 | -- |  | 75 | Δtm | Logarithmic Mean Temperature Difference for Dry Portion of Coil |  |  | Δtm = ((t1-tg2)-(tB-tgB)) /(ln((t1-tg2)/(tB-tgB))) | °F | #DIV/0!
76 | -- |  | 76 | AcD | Calculated External Surface Area for Dry Portion of Coil |  |  | AcD = qtD*(RaD+RmD+Rg)/Δtm | ft.2 | #DIV/0!
77 | 70 |  | 77 | qtW | Capacity for Wet Portion of Coil |  |  |  | -- | --
[6 empty] | For Partially Wet Coil |  | qtW = qt-qtD | Btuh | #DIV/0!
[6 empty] | For Fully Wet Coils |  | qtW = qt | Btuh | 0
78 | 71 |  | 78 | ts1 | Surface Temperature at Air Entering Side of Wet Portion. With: -Ps, h1, tg2, and C for Fully Wet Coil Also, tsB = t"1 for Partially Dry Coils |  |  |  | °F
79 | 72 |  | 79 | ts2 | Surface Temperature at Air Leaving Side of Wet Portion. With: - tg1, Ps, h2, and C |  |  |  | °F
80 | 73 |  | 80 | hs1 | Enthalpy of Saturated Air at Ps & ts1 |  |  |  | Btu/lb
81 | 74 |  | 81 | hs2 | Enthalpy of Saturated Air at Ps and ts2 |  |  |  | Btu/lb
82 | 75 |  | 82 | Δhm | Logarithmic Mean Enthalpy Difference Between Air Stream and Wetted Surface |  |  |  | -- | --
[6 empty] | For Fully Wet Coils |  | Δhm=((h1-hs1)-(h2-hs2)) /(ln((h1-hs1)/(h2-hs2))) | Btu/lb | #DIV/0!
[6 empty] | For Partially-Wet Coils |  | Δhm=((hB-hs1)-(h2-hs2)) /(ln((hB-hs1)/(h2-hs2))) | Btu/lb | #DIV/0!
83 | 76 |  | 83 | AcW | Calculated External Surface Area for Fully Wet Coil or Wet Portion of Coil |  |  | AcW, IP = 0.243*RmD*qtW/Δhm | ft.2 | #DIV/0!
84 | 77 |  | 84 | Ac | Total Calculated External Surface Area Note: For Case I and II in [28], complete [79]. For Case III in [28], complete [80] and [81]. |  |  |  | -- | --
[6 empty] | For Partially Wet Coil |  | Ac = AcW+AcD | ft.2 | #DIV/0!
[6 empty] | For Fully Wet Coils |  | Ac = AcW | ft.2 | #DIV/0!
85 | 78 |  | 85 | Nr | Required Number of Rows of Coil Tubes in Direction of Air Flow |  |  | Nr = Ac/Af*[8] | -- | #VALUE!
86 | 79 |  | 86 |  | If Ac > or < Ao, assume a new value of qt that's > or < [31]. Repeat calculations from step [26] through [78]. Plot calculated values of Ac against assumed values of [31] as shown in Fig. F410-9.1 |  |  |  | --
87 | 80 |  | 87 |  | Determine the actual value of qt from plot [86] with Ac = Ao |  |  |  | Btuh
88 | 81 | CALC TO DETERMINE AIR LEAVING DRY-BULB TEMP | 88 | c | Heat Transfer Exponent |  |  | c, IP = (Ao*60)/(14.58*RaD*60wa) | -- | #DIV/0!
89 | 82 |  | 89 | e-c | Heat Transfer Factor |  |  | e-c | -- | #DIV/0!
90 | 83 |  | 90 | h2 | Leaving Air Enthalpy at Actual Value of qt |  |  | h2 = h1-(([35] or [87])/60wa) | Btu/lb | #DIV/0!
91 | 84 |  | 91 | hs | Saturated Enthalpy at Effective Surface Temperature |  |  | hs = h1-((h1-([34] or [90])) /(1.0-e-c)) | Btu/lb | #DIV/0!
92 | 85 |  | 92 | ts | Effective Surface Temperature from Psychrometric Chart with Ps and hs |  |  |  | °F
93 | 86 |  | 93 | t2 | Air Leaving Dry-Bulb Temperature |  |  | t2 = ts+(t1-ts)*e-c | °F | #DIV/0!
94 | 87 | AIR-SIDE FRICTION CALCULATIONS | 94 | ΔPsw /Nr | Air-Side Friction per Row Deep at Standard Conditions (Use wet surface for partially dry and fully wet coils) - From Fig. 17 with Va |  |  |  | in. H20 /row
95 | 88 |  | 95 | Fa | Dry Surface Air-Side Pressure Drop Correction Factor |  |  | Fa, IP = (460+0.5*(t1+t2)) /(17.71*Ps) | -- | #DIV/0!
96 | 89 |  | 96 | (ΔPa) JOB | Air-Side Friction at JOB Conditions (constant wa) |  |  | (ΔPa)JOB = [94]*[95]*([5] or [85]) | in. H20 | #DIV/0!
97 | 90 | TUBE-SIDE PRESSURE DROP CALCULATIONS | 97 | f' | Friction Factor for Ethylene Glycol Solution (From Fig. 3 at Re) |  |  |  | --
98 | 91 |  | 98 | Δpt /Le | Ethylene Glycol Solution Pressure Drop Inside Tubes |  |  | Δpt /Le, IP= (f'*Vg2*[52])/(1.34*Di) | ft. Gly/ ft. tube | #DIV/0!
99 | 92 |  | 99 | Δph | Header and Tube Entrance and Exit Loss -Established by the manufacturer |  |  |  | ft. of Glyc
100 | 93 |  | 100 | (ΔPg) JOB | Ethylene Glycol Pressure Across Coil at Job Conditions |  |  | (ΔPg)JOB = (Le*[98])+[99] | ft. of Glyc | #DIV/0!
Figure F410-9.1