## Revision History
AHRI Combustion Equation Calculator
December 2012
Content Revision History
Rev | Date | Description | Author(s)
A | 12.13.12 | Create preliminary calculator using AHRI combustion equation set. IP version | DJD/DK
B | 12.18.12 | Add pull down for fuel, modify spreadsheet to take O2 or CO2 as input, and add some additional input description | DJD/DK
C | 12.18.12 | Added O2/CO2 update in output section | DJD/DK
D | 2.13.13 | Preliminary mods for net calculations and misc changes | DJD/DK

## AHRI Combustion Eqn
December 2012
AHRI- 1260 P Combustion Calculations
Select O2 or CO2
ENTER THE INPUTS: |  |  | O2 (%) | CO (ppm) | STK TEMP (F) | AIR TEMP (F) | FUEL | O2 Ref
|  |  | 10 | 0 | 300 | 70 | NG | 3
INTERMEDIATE CALCULATIONS: |  |  | CO2 (%) | O2 (%) | EA | Delta T | DFL | WFL | UBL | HR(a) | HR(s) | Hcond
|  |  | 6.1541 | 10 | 91.7431 | 230 | 7.0636 | 11.0229 | 0 | 0.013334 | 0.3 | 922.24
[7 empty] | DFLnet | DFLnet | UBLnet
|  |  | M(a) | M(fg) | M(wa) | M(wfg) | M(wc) | Ceff
|  |  | 30.0461 | 29.0261 | 0.20032 | 8.7078 | -6.4775 | 0
Ceffnet
OUTPUT:
|  |  | CO2 (%) | EA (%) | Gross EFF (%) | COAF (ppm) | CO (3) | SL (%)
|  |  | 6.1541 | 91.7431 | 81.9135 | 0 | 0 | 18.0865
Fuel Table
Item | NG |  |  | NG | OIL 2 | OIL 6 | Propane
C (% wt) | 0.694 |  | Carbon | 0.694 | 0.873 | 0.886 | 0.816
H (%wt) | 0.225 |  | Hydrogen | 0.225 | 0.125 | 0.093 | 0.184
S (%wt) | 0 |  | Sulfur | 0 | 0.0021 | 0.0085 | 0
K1 | 0.189 |  | K1 | 0.189 | 0.275 | 0.293 | 0.227
K2 | 11.8 |  | K2 | 11.8 | 15.7 | 16.7 | 13.8
K3 | 5.43 |  | K3 | 5.43 | 3.33 | 2.6 | 4.34
K4 | 32 |  | K4 | 32 | 47 | 50 | 38
HHV (BTU/lb) | 21830 |  | HHV | 21830 | 18993 | 18126 | 21573
M(wf) (Lb H2O/Lb Fuel) | 2.03 |  | M(wf) | 2.03 | 1.17 | 0.86 | 1.66
M(as) Lb Air/ Lb Fuel | 15.67 |  | M(as) | 15.67 | 14.29 | 13.34 | 15.66
M(fgs) Lb FG / Lb Fuel | 14.65 |  | M(fgs) | 14.65 | 14.17 | 13.51 | 15
Definitions
K1 | Dry flue gas constant, gross basis ( Cp = 0.257 BTU/Lb R or 7.19 BTU/Lbmol R)
K2 | CO2 theoretical maximum constant
K3 | Wet Flue gas constant
K4 | Unburned Carbon loss constant
EA | Excess air approximation
CO2 | Carbon Dioxide in fluegas (%)
COAF | Carbon Monoxide air free (ppm)
O2 | Oxygen, measured in flue gas (%)
Delta T | Net Stack temperature (F)
T(f) | Flue Temperature (F)
T(i) | Inlet Temperature (F)
DFL | Dry flue gas loss, gross basis (%)
WFL | Wet Flue gas loss, gross basis (%)
UBL | Unburned carbon loss (%)
HR(a) | Humidity Ratio for combustion air (Lb H2O / Lb dry air)
HR(s) | Humidity Ratio for flue gas (Lb H2O / Lb dry air)
Hcond | Heat of condensation (BTU / Lb H2O)
M(a) | Mass of combustion air (Lb air/ Lb fuel)
M(fg) | Mass of flue gas (Lb of dry flue gas / Lb air)
M(wa) | Mass of water vapor in combustion air (Lb H2O / Lb fuel)
M(wfg) | Mass of water vapor remaining in flue gas (Lb H2O / Lb fuel)
M(wc) | Mass of condensate (Lb H2O / Lb fuel)
M(as) | Stoichiometric mass of combustion air (Lb H2O /Lb fuel)
M(fgs) | Stoichiometric mass of flue gas (Lb H2O /Lb fuel)
M(wf) | Mass of water generated from fuel (Lb H2O / Lb fuel)
Ceff | Gain in efficiency due to condensation of water vapor (%)
HHV | Higher Heating Value of fuel (BTU / Lb fuel)

## Humidity Ratio
Humidity Ratio
T(F) | LbH2O/Lb Dry Air
23 | 0.0025
32 | 0.0038
41 | 0.0054
50 | 0.0077
59 | 0.011
68 | 0.015
77 | 0.02
86 | 0.027
95 | 0.037
104 | 0.049
113 | 0.065
122 | 0.087
131 | 0.12
140 | 0.15
149 | 0.21